## Changelog
Rev | Date | By | Includes
D | 2014-11-17 | JWE | Updated rep list. Checked table values in ASHRAE 2014 Refrigebook for suction, discharge, and Liquid line Capacities
F | 2016-01-08 | JWE | Updated Rep list. Included Suction Trap diagram
G | 2016-05-20 | JWE | Updated recommended oil to add to system in piping notes
H | 2016-04-25 | JWE | Updated dropdown menus to include Digital scroll option. Added CDI/Updated to rep roster
I | 2019-02-19 | JWE | Added 60ft riser details and changed HGBP logic to consider minimum valve position
J | 2019-04-08 | JWE | Updated dropdown menu to have new single circuit options
6 | TBD | JWE | Update Discharge line logic (see notes); Add Refrigerant charge estiamte (3rd page); Update notes to say Max combined suction riser to 60, trap and bleed with diagram

## R-410A_Calculator
REFRIGERANT PIPING REVIEW | [8 empty] | Circuit #+MM:M | Superheat | Condensing Temp | Discharge Temp | Fittings | Refrigeration |  |  | Reps | RCS | Capacity | Staging
[9 empty] | #1 | oF | oF | oF | Click here to select fitting. | 1658.7457 | lb/h min. refrigerant flow @ 45°F SST
Job Name: |  | 20241002001 - Inspira IMC Mannington Pharmacy |  |  |  | Rep Office: | TriState HVAC Equipment, LLP |  | #2 | 10 | Select |  | 90° Std Elbow | 71.51 | lb/c.f. density of liquid refrigerant @ 45°F |  | Air Cond. Equip. Sales, Inc. | RCS06F-079 | Nominal = 6.5 tons (CKT#1 = 1 - 6.5 ton compressor) | Staging = 0-100
Job Description: |  | DCSA040 (fixed speeds on both circuit) coupled with Skyline DXG12C12 |  |  |  | Sales Person: | Mark Lombardi |  | Identical Circuits (1=2) |  | 80 |  | 90° Long Radius Elbow | 0.3866 | CFM of liquid refrigerant |  | Air Reps | RCS07G-091 | Nominal = 7.5 tons (CKT#1 = 1 - 7.5 ton compressor) | Staging = 0-100
Model Number: | [5 empty] | Date: | 2025-03-12 |  | Fixed Scroll on #1, Digital Scroll on #2 |  | 90 |  | 90° Street Elbow | 2.318 | lb/c.f. density of refrigerant vapor @ 55°F |  | Air Tech Equipment Inc. | RCS10G-121 | Nominal = 10 tons (CKT#1 = 1 - 10 ton compressor, two stage) | Staging = 0-100
Circuit #: |  | Identical Circuits (1=2) | [8 empty] | 100 |  | 45° Std Elbow | 11.9264 | CFM of refrigerant vapor, Suction |  | Airetech Corp. | RCS11F-125 | Nominal = 10 tons (CKT#1 = 2 - 5 ton compressors) | Staging = 0-50-100
[11 empty] | 110 |  | 45° Street Elbow | 8.9767 | lb/c.f. density of saturated refrigerant vapor @ 125°F |  | Allegheny Engineering Co. | RCS12F-150 | Nominal = 12.5 tons (CKT#1 = 2 - 6.3 ton compressors) | Staging = 0-50-100 | 426725
Refrigerant |  |  | R-410A | [7 empty] | 120 |  | 180° Std Elbow | 8.206 | lb/c.f. density of superheated refrigerant vapor @ 180°F |  | Applied Air Engineering, Inc. | RCS15F-180 | Nominal = 15 tons (CKT#1 = 2 - 7.5 ton compressors) | Staging = 0-50-100 | 213362.5
Circuit Cooling Capacity |  |  | 17.8 | TONS | CKT#1 = 2 fixed speed compressors, CKT#2 = 2 fixed speed compressors | [5 empty] | 130 |  | Flow Through Branch | 3.369 | CFM of refrigerant vapor |  | Briggs Equipment Sales | RCS20F-240 | Nominal = 20 tons (CKT#1 = 2 - 10 ton compressors) | Staging = 0-50-100 | 17.7802
Minimum Circuit Cooling Capacity |  |  | 8.9 | TONS | Staging = 0-25-50-75-100 | [7 empty] | Straight-Through Flow No Reduction |  |  |  | Brooks Air Systems, Inc. | RCS015D | Nominal = 15 tons (CKT#1 = 1 - 7 ton compressor, CKT#2 = 1 - 7 ton compressor) | Staging = 0-50-100
Condensing Temperature |  |  | 120 | oF | Assumed | [7 empty] | Straight-Through Flow Reduced 1/4 |  | Type L | Cross Section | Carroll Air Systems, Inc. | RCS016D | Nominal = 15 tons (CKT#1 = 1 - 7 ton compressor, CKT#2 = 1 - 7 ton compressor) | Staging = 0-50-100
Saturated Suction Temperature (SST) |  |  | 40 | oF | Enter Value between -60oF & 40oF | [7 empty] | Straight-Through Flow Reduced 1/2 | Pipe size O.D. | I.D. | (SF) | CDI | RCS020D | Nominal = 20 tons (CKT#1 = 1 - 10 ton compressor, CKT#2 = 2 - 4.5 ton compressors) | Staging = 0-25-50-75-100
Superheat |  |  | 10 | oF | Assumed | [7 empty] | Globe or Solenoid Valve | 0.5 | 0.43 | 0.0010085 | Climatec, Inc. | RCS020D (Digital) | Nominal = 20 tons (CKT#1 = 1 - 10 ton Fixed Speed, CKT#2 = 1 - 10 ton Digital Scroll) | Modulating Control with Digital Compressor
Discharge Refrigerant Temperature |  |  | 180 | oF | Required if designing discharge line. | [7 empty] | 60° Wye Valve | 0.625 | 0.545 | 0.00162 | Controls & Equipment | RCS021D | Nominal = 20 tons (CKT#1 = 1 - 10 ton compressor, CKT#2 = 2 - 4.5 ton compressors) | Staging = 0-25-50-75-100
(Circuit cooling capacity based off Refrigeration Effect from condenser tech data sheets) | [12 empty] | 45° Wye Valve | 0.75 | 0.666 | 0.0024192 | D & B Eng. of New Jersey, Inc. | RCS025D | Nominal = 25 tons (CKT#1 = 1 - 11.5 ton compressor, CKT#2 = 2 - 5.5 ton compressors) | Staging = 0-25-50-75-100
|  | LIQUID LINE | [10 empty] | Angle Valve | 0.875 | 0.785 | 0.003361 | Daikin Applied Birmingham | RCS025D (Digital) | Nominal = 25 tons (CKT#1 = 1 - 11.5 ton Fixed Speed, CKT#2 = 1 - 11.5 ton Digital Scroll)) | Modulating Control with Digital Compressor
[13 empty] | Gate Valve | 1.125 | 1.025 | 0.0057303 | Daikin Applied Atlanta | RCS026D | Nominal = 25 tons (CKT#1 = 1 - 11.5 ton compressor, CKT#2 = 2 - 5.5 ton compressors) | Staging = 0-25-50-75-100
|  | Fitting/Valve Losses in Equivalent Feet of Pipe |  |  |  | Table Data | [6 empty] | Swing Check | 1.375 | 1.265 | 0.0087279 | Daikin Applied New York | RCS030D | Nominal = 30 tons (CKT#1 = 1 - 13 ton compressor, CKT#2 = 2 - 6 ton compressors) | Staging = 0-25-50-75-100
|  | Accessory | Quantity | Equivalent Losses |  | Table Le | 100 | FEET |  |  |  |  | Sight Glass | 1.625 | 1.505 | 0.012354 | Daikin Applied South Florida | RCS030D (Digital) | Nominal = 30 tons (CKT#1 = 1 - 13 ton Fixed Speed, CKT#2 = 1-13 ton Digital Scroll) | Modulating Control with Digital Compressor
|  | 90° Std Elbow | 8 | 12 | FEET | Table Dt | 1 | oF |  |  |  |  | Filter Drier | 2.125 | 1.985 | 0.021491 | Daikin Applied Latin America | RCS031D | Nominal = 30 tons (CKT#1 = 1 - 13 ton compressor, CKT#2 = 2 - 6 ton compressors) | Staging = 0-25-50-75-100
|  | 45° Std Elbow | 0 | 0 | FEET | Table DP | 4.75 | PSI |  |  |  |  | Suction Filter | 2.625 | 2.465 | 0.033141 | ElitAir, Inc. | RCS035D | Nominal = 35 tons (CKT#1 = 2 - 7.5 ton compressors, CKT#2 = 2 - 7.5 ton compressors) | Staging = 0-25-50-75-100
|  | Globe or Solenoid Valve | 1 | 17.5 | FEET | Table Capacity | 14.3 | TONS |  |  |  |  | Other | 3.125 | 2.945 | 0.047304 | Engineered Equipment, Inc. | RCS040D | Nominal = 40 tons (CKT#1 = 2 - 8.5 ton compressors, CKT#2 = 2 - 8.5 ton compressors) | Staging = 0-25-50-75-100
|  | Sight Glass | 1 | 1.1 | FEET | Actual / Operating Conditions | [7 empty] | 3.625 | 3.425 | 0.063981 | Enviroair Industries Inc. | RCS042D | Nominal = 40 tons (CKT#1 = 2 - 8.5 ton compressors, CKT#2 = 2 - 8.5 ton compressors) | Staging = 0-25-50-75-100
|  | Filter Drier | 1 | 13.5 | FEET | Actual Le | 116.1 | FEET | [5 empty] | 4.125 | 3.905 | 0.083171 | Ewing/Kessler Mech Solutions | RCS045D | Nominal = 40 tons (CKT#1 = 2 - 10 ton compressors, CKT#2 = 2 - 10 ton compressors) | Staging = 0-25-50-75-100
|  | Click here to select fitting. | 0 | 0 | FEET | Actual Dt | 1.7218 | oF | [5 empty] | 5.125 | 4.875 | 0.12962 | Gardiner | RCS050D | Nominal = 50 tons (CKT#1 = 2 - 11.5 ton compressors, CKT#2 = 2 - 11.5 ton compressors) | Staging = 0-25-50-75-100
[6 empty] | Actual DP | 8.1786 | PSI | [5 empty] | 6.125 | 5.845 | 0.18634 | Global Mechanical Sys. Ltd. | RCS051D | Nominal = 50 tons (CKT#1 = 2 - 11.5 ton compressors, CKT#2 = 2 - 11.5 ton compressors) | Staging = 0-25-50-75-100
|  | Length of Straight Pipe |  | 60 | FEET | Line Capacity | 17.7611 | TONS | [5 empty] | 8.125 | 7.725 | 0.32548 | Global Price Mechanical | RCS060D | Nominal = 60 tons (CKT#1 = 2 - 13 ton compressors, CKT#2 = 2 - 13 ton compressors) | Staging = 0-25-50-75-100
|  | Velocity at Rated Circuit Capacity | Acceptable | 319.6067 | Feet/Min. | Size of Liquid Line | 0.75 | INCHES | [8 empty] | H.V.A.C. Sales, Ltd. | RCS062D | Nominal = 60 tons (CKT#1 = 2 - 13 ton compressors, CKT#2 = 2 - 13 ton compressors) | Staging = 0-25-50-75-100
|  | Calculations Based on Ch. 1, 2014 ASHRAE Handbook REFRIGERATION | [14 empty] | Harrison Energy Partners | RCS063D | Nominal = 60 tons (CKT#1 = 2 - 13 ton compressors, CKT#2 = 2 - 13 ton compressors) | Staging = 0-25-50-75-100
[17 empty] | Havtech | RCS068D | Nominal = 70 tons (CKT#1 = 2 - 15 ton compressors, CKT#2 = 2 - 15 ton compressorss) | Staging = 0-25-50-75-100
|  | SUCTION LINE | [14 empty] | Heaven Engineering Co. | RCS070D | Nominal = 70 tons (CKT#1 = 3 - 10 ton compressors, CKT#2 = 3 - 10 ton compressors) | Staging = 0-16-33-50-67-83-100
[17 empty] | Hoffman & Hoffman, Inc. | RCS071D | Nominal = 70 tons (CKT#1 = 3 - 10 ton compressors, CKT#2 = 3 - 10 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Fitting/Valve Losses in Equivalent Feet of Pipe |  |  |  | Table Data - Horizontal Pipe | [10 empty] | HTS New England | RCS072D | Nominal = 70 tons (CKT#1 = 3 - 10 ton compressors, CKT#2 = 3 - 10 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Accessory | Quantity | Equivalent Losses |  | Table Le | 100 | FEET | [8 empty] | HTS Engineering Ltd. | RCS075D | Nominal = 75 tons (CKT#1 = 3 - 11.5 ton compressors, CKT#2 = 3 - 11.5 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | 90° Std Elbow | 8 | 26.4 | FEET | Table Dt | 2 | oF | [8 empty] | I.T.C. Technologies | RCS079D | Nominal = 80 tons (CKT#1 = 3 - 11.5 ton compressors, CKT#2 = 3 - 13 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | 45° Std Elbow | 0 | 0 | FEET | Table DP | 4.5063 | PSI | [8 empty] | Indiana Thermal Solutions | RCS080D | Nominal = 80 tons (CKT#1 = 3 - 11.5 ton compressors, CKT#2 = 3 - 11.5 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Click here to select fitting. | 0 | 0 | FEET | Table Capacity | 13.74 | TONS | [8 empty] | Kehoe Equipment Ltd. | RCS081D | Nominal = 80 tons (CKT#1 = 3 - 11.5 ton compressors, CKT#2 = 3 - 11.5 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | (Assumes ?? traps) |  |  |  | Actual / Operating Conditions - Horizontal Pipe | [10 empty] | Long Building Tech | RCS085D | Nominal = 85 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 13 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Length of Horizontal Suction Pipe |  | 55 | FEET | Actual Le | 93.4 | FEET | [8 empty] | M & M Engineering Limited | RCS090D | Nominal = 90 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 13 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Horizontal Suction @ Min CKT Capacity | Acceptable | 1366.4705 | Ft. / Min | Actual Dt | 2.9768 | oF | [8 empty] | Mason & Barry, Inc. | RCS091D | Nominal = 90 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 13 ton compressors) | Staging = 0-16-33-50-67-83-100
[6 empty] | Actual DP | 6.7073 | PSI | [8 empty] | Masters Building Solutions | RCS092D | Nominal = 90 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 13 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Determine Size of Suction Riser for Minimum Capacity |  |  |  | Line Capacity | 17.754 | TONS | [8 empty] | McQuay National Accts | RCS100D | Nominal = 100 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 15 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Minimum Capacity of HVAC Unit |  | 8.9 | TONS | Size of Suction Line | 1.375 | INCHES | [8 empty] | McQuay Caribe Inc | RCS101D | Nominal = 100 tons (CKT#1 = 3 - 13 ton compressors, CKT#2 = 3 - 15 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Size of Suction Line Riser |  | 1.375 | INCHES | [11 empty] | Mechanical Conmponents Limited | RCS105D | Nominal = 105 tons (CKT#1 = 3 - 15 ton compressors, CKT#2 = 3 - 15 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Length of Vertical Suction Riser (MAX 60 ft total) |  | 5 | FEET | Table Data - Suction Riser | [10 empty] | Mechanical Concepts, LLC | RCS110D | Nominal = 110 tons (CKT#1 = 3 - 15 ton compressors, CKT#2 = 3 - 15 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Vertical Suction Riser, @ Min. CKT Capacity | Acceptable | 1366.4705 | Ft. / Min | Table Le | 100 | FEET | [8 empty] | Mechanical Products Intermountain | RCS120D | Nominal = 120 tons (CKT#1 = 3 - 15 ton compressors, CKT#2 = 3 - 20 ton compressors) | Staging = 0-16-33-50-67-83-100
[6 empty] | Table Dt | 2 | oF | [8 empty] | Mechanical Resource Group | RCS125D | Nominal = 125 tons (CKT#1 = 3 - 20 ton compressors, CKT#2 = 3 - 20 ton compressors) | Staging = 0-16-33-50-67-83-100
[6 empty] | Table DP | 4.5063 | PSI | [8 empty] | Mechanical Sales, Inc. | RCS130D | Nominal = 130 tons (CKT#1 = 3 - 20 ton compressors, CKT#2 = 3 - 20 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Actual / Operating Conditions - Total |  |  |  | Table Capacity | 13.7368 | TONS | [8 empty] | Mid-South Equipment | RCS140D | Nominal = 140 tons (CKT#1 = 3 - 20 ton compressors, CKT#2 = 3 - 25 ton compressors) | Staging = 0-16-33-50-67-83-100
|  | Actual Dt |  | 3.1363 | oF | Actual / Operating Conditions - Suction Riser | [10 empty] | Midwest Engineering Ltd.
|  | Actual DP |  | 7.0665 | PSI | Actual Le | 5 | FEET | [8 empty] | Modular Comfort Systems, Inc.
|  | Size of Horizontal Suction Line |  | 1.375 | INCHES | Actual Dt | 0.15943 | oF | [8 empty] | Norbryhn Equipment Company
|  | Size of Vertical Suction Riser |  | 1.375 | INCHES | Actual DP | 0.35921 | PSI | [8 empty] | Norman Wright Mech. Equip. Corp.
|  | Minimum Capacity for Vertical Suction Riser |  | 3.1274 | TONS | Line Capacity | 17.7539 | TONS | [8 empty] | Norman S. Wright-Climatec Mech
|  | Calculations Based on Ch. 1, 2014 ASHRAE Handbook REFRIGERATION | [14 empty] | O'Connell Inc., R.P.
O'Connor Company
|  | HOT GAS BYPASS LINE | [14 empty] | Olympic International Agy, Ltd.
Perry Mechanical Systems
|  | Estimate HGBP Valve Capacity |  |  |  | Table Data | [10 empty] | Schwab-Vollhaber-Lubratt, Inc.
|  | Minimum Compressor Capacity |  | 8.9 | Tons | Table Le | 100 | FEET | [8 empty] | Stinebaugh & Company
|  | Min. System Capacity (if unknown estimate 5 tons) |  | 4.45 | Tons | Table Dt | 1 | oF | [8 empty] | Swan Associates, Inc.
|  | HGBP Valve Capacity |  | 4.45 | Tons | Table DP | 4.75 | PSI | [8 empty] | Thermal Environment Sales
|  | Velocity at HGBP Valve Capacity |  | 1039.7986 | Ft. / Min | Table Capacity | 2.7279 | TONS | [8 empty] | Thermal Equipment
[6 empty] | Actual / Operating Conditions | [10 empty] | Thermal Mechanics, Inc.
|  | Fitting/Valve Losses in Equivalent Feet of Pipe |  |  |  | Actual Le | 100.2 | FEET | [8 empty] | Thermal Mechanics, Inc. - KC
|  | Accessory | Quantity | Equivalent Losses |  | Actual Dt | 2.4178 | oF | [8 empty] | Thermal-Netics, Inc.
|  | 90° Std Elbow | 8 | 11.2 | FEET | Actual DP | 11.4843 | PSI | [8 empty] | Thermaltech
|  | 45° Std Elbow | 0 | 0 | FEET | Line Capacity | 4.4283 | TONS | [8 empty] | Thermosystems, Inc.
|  | Globe or Solenoid Valve | 1 | 17 | FEET | Size of HGBP Line | 0.625 | INCHES | [8 empty] | T.P. Woodside Inc
TriState HVAC Equipment, LLP
|  | Length of Straight Pipe |  | 60 | FEET | [11 empty] | Varitech Solutions
|  | Calculations Based on Ch. 1, 2014 ASHRAE Handbook REFRIGERATION | [13 empty] | Anything below is hidden | Vemco, Inc.
DISCHARGE LINE
|  | Fitting/Valve Losses in Equivalent Feet of Pipe |  |  |  | Table Data - Horizontal Pipe
|  | Accessory | Quantity | Equivalent Losses |  | Table Le | 100 | FEET
|  | 90° Std Elbow | 8 | 26.4 | FEET | Table Dt | 1 | oF
|  | 45° Std Elbow | 0 | 0 | FEET | Table DP | 4.75 | PSI
|  | Click here to select fitting. | 0 | 0 | FEET | Table Capacity | 25.0776 | TONS
Actual / Operating Conditions - Horizontal Pipe
|  | Length of Horizontal Discharge Pipe |  | 60 | FEET | Actual Le | 98.4 | FEET
|  | Horizontal Discharge @ Min CKT Capacity | Too Low | 386.0034 | Ft. / Min | Actual Dt | 0.53093 | oF
[6 empty] | Actual DP | 2.5219 | PSI
|  | Determine Size of Discharge Riser for Minimum Capacity |  |  |  | Line Capacity | 17.8611 | TONS
|  | Minimum Capacity of HVAC Unit |  | N/A | TONS | Size of Discharge Line | 1.375 | INCHES
|  | Size of Discharge Line Riser |  | N/A | INCHES
|  | Length of Vertical Discharge Riser |  | 0 | FEET | Table Data - Discharge Riser
|  | Vertical Discharge Riser, @ Min. CKT Cap. | #N/A | #N/A | Ft. / Min | Table Le | 100 | FEET
[6 empty] | Table Dt | 1 | oF
|  | Actual / Operating Conditions - Total |  |  |  | Table DP | 4.75 | PSI
|  | Actual Dt |  | 0.53093 | oF | Table Capacity | 25.0776 | TONS
|  | Actual DP |  | 2.5219 | PSI | Actual / Operating Conditions - Discharge Riser
|  | Size of Horizontal Discharge Line |  | 1.375 | INCHES | Actual Le | 0 | FEET
|  | Size of Vertical Discharge Riser |  | N/A | INCHES | Actual Dt | 0 | oF
|  | Minimum Capacity for Vertical Discharge Riser |  | N/A | TONS | Actual DP | 0 | PSI
[6 empty] | Line Capacity | N/A | TONS
Calculations Based on Ch. 2, 2006 ASHRAE Handbook REFRIGERATION
Also, please reference notes below:
• Refer to installation manual 903 (C vintage), 914-4 (D vintage), or 962 (F vintage), and Application Guide 31-011 for equipment installation and piping requirements. The installation manuals include recommendations for best piping practices, and are summarized below.
equipment installation and piping requirements. The installation manuals include recommendations for best
piping practices, and are summarized below.
• Daikin does not size or design piping. We can only review completed drawings and make recommendations based on
the submitted data. Submitted data should be complete and include pipe sizing, components, elevations, tie-ins,
refrigerant, design conditions, etc...
• Based on the submitted data and assuming R410A and normal operating conditions see the attached documents for
liquid and suction line sizes for the spilt condensing unit(s).
• Avoid installing refrigerant lines under ground.
• Slope all refrigerant lines 1/8" per foot in the direction of flow.
• Use one liquid line solenoid per circuit and one TXV per liquid connection on evaporator coil(s).
• Size TXVs based on actual design conditions rather than nominal rating to insure adequate turn-down controls.
• Filter drier should be just before liquid line solenoid valve.
• Install the liquid line solenoid valve near the evaporator.
• Install the sight glass near the thermal expansion valve.
• Install a trap at the bottom of any suction or discharge gas riser. Include additional suction traps at 20’ intervals on units with fixed speed
scrolls. Digital scroll compressor circuits need traps at 10' intervals. This reduced height will allow oil return even with minimum
compressor ON time. Note: Maximum recommended vertical suction riser is 60 ft
• Double riser should never be used.
• If the evaporator coil is higher than the condenser, install a suction riser inverted trap to prevent liquid flooding.
• If the evaporator coil is higher than the condenser, install a check valve near the condenser to prevent liquid floodback
into the condenser during off periods.
• Transitions in pipe sizes should be done as not to impede oil return.
• Service taps or valve should be installed as required for service and testing purposes.
• Suction and HGBP lines should be insulated. Liquid lines should be insulated if heat pickup will affect subcooling.
• If HGBP is installed, pipe directly into the suction line per IM 914-5, page 24, figure 19. The sensing bulb for the TXV
should be moved and placed at least 3 feet down from where the hot gas bypass is introduced.
• System will require additional refrigerant and oil. Industry standard is to add oil weight equal to 2-3% of
TOTAL refrigerant weight (i.e. 100lbs of refrigerant = 2-3 lbs of oil).
• It is the responsibility of the installing contractor and start-up technician to ensure adequate liquid subcooling for any
vertical risers in the liquid line(s). Recommended minimum subcooling is 6°F at the expansion device, plus piping
pressure drop and risers.
R410A: 1°F subcooling per 4.7 PSI pipe pressure drop & 1°F of subcooling per 9.1 ft. of riser.
Figure 3 - Standard Refrigeration Suction Line Trap

## R-410A_Data
2006 ASHRAE Handbook Refrigeration |  |  |  |  | Table Data |  | Inputs |  | Calculated Data |  | Curve Fit Data
Table 8 Suction, discharge, and Liquid Line Capacities in Tons for Refrigerant 410A | [36 empty] | Determines Minimum Suction Line Size
Line Size | Suction Lines (Dt = 2oF) |  |  |  |  | Discharge Lines (Dt = 1oF, Dp = 4.75 psi) |  | Line Size | Liquid Lines |  |  | Determines Minimum Liquid Line Size | [7 empty] | Info Found Below Table 8 |  |  |  | Interpolation of Suction & Discharge Multipliers | [8 empty] | Table 8 - Curve Fit w/ Suction Multiplier |  |  |  | Suction Line Capacity | Look Up Sufficient Suction Line Capacity | Determine Minimum Suction Line Capacity | Corresponding Suction Line Size, OD
| Saturated Suction Temperature, oF | [7 empty] | See notes a |  |  | Look Up Sufficient Liquid Line Capacities | Line Size | Determine Minimum Liquid Line Capacity | Corresponding Liquid Line Size, OD | Suction Line Curve Fit |  |  |  | Condensing Temperature | Suction Line | Discharge Line |  | Act. Cond. Temp. | Min # for Interpolation | Max # for Interpolation | Known x's | Known y's Suction | Known y's Discharge | Suction Line | Discharge Line |  | SST | Curve Fit | Suction Line Capacity | Type L Copper, OD
Type L Copper, OD | -40 | -20 | 0 | 20 | 40 | Saturated Suction Temperature, oF |  | Type L Copper, OD | Vel = | Dt = 1oF |  |  | Type L Copper, OD |  |  | SST | Curve Fit | Type L Copper, OD | Suction Line Capacity | [13 empty] | oF | Dp (psi/100ft) |  |  | tons
| Corresponding Dp, psi/100ft | [7 empty] | fpm | Dp (psi) = | [5 empty] | oF | Dp (psi/100ft) |  |  | oF | multiplier | multiplier |  | oF | [5 empty] | multiplier | multiplier |  | 40 | 4.5063 | tons |  | 17.8
| 1.27 | 1.85 | 2.57 | 3.46 | 4.5 | -40 | 40 |  | 100 | 4.75 | [5 empty] | 40 | 4.5063 |  | tons | 80 | 1.17 | 0.815 |  | 120 | 80 |  | 120 | 0.889 | 1.096 | 0.889 | 1.096 |  |  |  | 0.78792 | 0.5 |  |  | 13.74 | 1.375
0.5 | 0.17 | 0.27 | 0.42 | 0.62 | 0.89 | 1.17 | 1.33 | 0.5 | 2 | 4.6 |  |  | 0.5 | 14.3 | 0.75 |  |  | 0.5 | 0.8863 | 90 | 1.104 | 0.889 |  |  | 90 |  | 120 | 0.889 | 1.096 | [5 empty] | 1.4455 | 0.625
0.625 | 0.31 | 0.51 | 0.79 | 1.17 | 1.67 | 2.2 | 2.49 | 0.625 | 3.2 | 8.6 |  |  | 0.625 |  |  |  |  | 0.625 | 1.626 | 100 | 1.035 | 0.963 |  |  | 100 | [9 empty] | 2.506 | 0.75
0.75 | 0.53 | 0.87 | 1.35 | 2 | 2.84 | 3.74 | 4.23 | 0.75 | 1.7 | 14.3 |  | 14.3 | 0.75 |  |  |  |  | 0.75 | 2.8189 | 110 | 0.964 | 1.032 |  |  | 110 | [9 empty] | 3.8491 | 0.875
0.875 | 0.83 | 1.35 | 2.08 | 3.08 | 4.39 | 5.76 | 6.52 | 0.875 | 6.7 | 22.6 |  | 22.6 | 0.875 |  |  |  |  | 0.875 | 4.3297 | 120 | 0.889 | 1.096 |  |  | 120 | 120 | [8 empty] | 7.9165 | 1.125
1.125 | 1.69 | 2.74 | 4.22 | 6.23 | 8.86 | 11.64 | 13.17 | 1.125 | 11.4 | 45.8 |  | 45.8 | 1.125 |  |  |  |  | 1.125 | 8.9049 | 130 | 0.808 | 1.16 |  |  |  | 130 | [8 empty] | 13.7368 | 1.375 |  | 13.74
1.375 | 2.95 | 4.78 | 7.34 | 10.82 | 15.41 | 20.21 | 22.88 | 1.375 | 17.4 | 79.7 |  | 79.7 | 1.375 |  |  |  |  | 1.375 | 15.452 | [15 empty] | 21.5725 | 1.625 |  | 21.5725
1.625 | 4.67 | 7.56 | 11.61 | 17.14 | 24.28 | 31.92 | 36.14 | 1.625 | 24.6 | 125.9 |  | 125.9 | 1.625 |  |  |  |  | 1.625 | 24.266 | [15 empty] | 44.5816 | 2.125 |  | 44.5816
2.125 | 9.71 | 15.71 | 24.05 | 35.45 | 50.19 | 65.88 | 75.57 | 2.125 | 42.8 | 260.7 |  | 260.7 | 2.125 |  |  |  |  | 2.125 | 50.148 | [15 empty] | 78.4249 | 2.625 |  | 78.4249
2.625 | 17.17 | 27.74 | 42.45 | 62.53 | 88.43 | 115.9 | 131.2 | 2.625 | 66 | 459.7 |  | 459.7 | 2.625 |  |  |  |  | 2.625 | 88.217 | [15 empty] | 124.9205 | 3.125 |  | 124.9205
3.125 | 27.44 | 44.24 | 67.77 | 99.53 | 140.83 | 184.62 | 208.98 | 3.125 | 94.2 | 733 |  | 733 | 3.125 |  |  |  |  | 3.125 | 140.518 | [15 empty] | 185.1538 | 3.625 |  | 185.1538
3.625 | 40.84 | 65.81 | 100.5 | 147.66 | 208.65 | 273.54 | 309.64 | 3.625 | 127.4 | 1087.5 |  | 1087.5 | 3.625 |  |  |  |  | 3.625 | 208.272 | [15 empty] | 260.7526 | 4.125 |  | 260.7526
4.125 | 57.58 | 92.66 | 141.61 | 208.22 | 293.7 | 385.08 | 435.9 | 4.125 | 165.7 | 1530.2 |  | 1530.2 | 4.125 |  |  |  |  | 4.125 | 293.31 | [15 empty] | 464.3087 | 5.125 |  | 464.3087
5.125 | 103.03 | 165.73 | 253.05 | 370.82 | 523.21 | 686.18 | 776.72 | 5.125 | 258.2 | 2729.8 |  | 2729.8 | 5.125 |  |  |  |  | 5.125 | 522.282 | [15 empty] | 745.238 | 6.125 |  | 745.238
6.125 | 166 | 266.14 | 405.75 | 594.85 | 839.82 | 1099.1 | 1244.13 | 6.125 | 371.1 | 4383.7 |  | 4383.7 | 6.125 |  |  |  |  | 6.125 | 838.288 | [15 empty] | 1537.8811 | 8.125 |  | 1537.8811
8.125 | 344.31 | 551.73 | 840.04 | 1229.69 | 1733.02 | 2268.62 | 2567.98 | 8.125 | 648.3 | 9049.5 |  | 9049.5 | 8.125 |  |  |  |  | 8.125 | 1729.9
Table is based on |  | 100 | feet of equivalent length, Le. | [16 empty] | Portion of Table 8
Suction Line Table Dt |  | 2 | oF | [16 empty] | Discharge Lines (Dt = 1oF, Dp = 3.05 psi) |  |  | Discharge Line Curve Fit |  | Curve Fit w/mulitplier |  | Determines Minimum Discharge Line Size |  |  |  |  | Determines Minimum HGBP Line Size
Liquid Line Table Dt |  | 1 | oF | [23 empty] | Discharge Line Capacity | Look Up Sufficient Discharge Line Capacity | Determine Minimum Discharge Line Capacity | Corresponding Discharge Line Size, OD |  | HGBP Line Capacity | Look Up Sufficient HGBP Line Capacity | Determine Minimum HGBP Line Capacity | Corresponding HGBP Line Size, OD
Discharge Line Table Dt |  | 1 | oF | [16 empty] | Saturated Suction Temperature, oF |  | SST | Discharge Line Capacity |  | Discharge Line Capacity | Type L Copper, OD
Discharge Line Table Dp |  | 4.75 | PSI | [18 empty] | oF |  |  |  |  | tons |  |  |  |  | tons
[20 empty] | -40 | 40 | 40 | tons |  | tons |  | 17.8 |  |  |  |  | 1.4833
[20 empty] | 1.17 | 1.33 |  | 1.33 |  | 1.4577 | 0.5 |  |  | 25.0776 | 1.375 |  |  |  | 2.7279 | 0.625
[20 empty] | 2.2 | 2.49 |  | 2.489 |  | 2.7279 | 0.625 | [6 empty] | 2.7279
[20 empty] | 3.74 | 4.23 |  | 4.229 |  | 4.635 | 0.75 | [6 empty] | 4.635
[20 empty] | 5.76 | 6.52 |  | 6.52 |  | 7.1459 | 0.875 | [6 empty] | 7.1459
Type L Copper | [19 empty] | 11.64 | 13.17 |  | 13.169 |  | 14.4332 | 1.125 | [6 empty] | 14.4332
OD | ID | Sq. Ft. | [17 empty] | 20.21 | 22.88 |  | 22.881 |  | 25.0776 | 1.375 |  | 25.0776 |  |  |  |  | 25.0776
0.5 | 0.43 | 0.0010085 | [17 empty] | 31.92 | 36.14 |  | 36.138 |  | 39.6072 | 1.625 |  | 39.6072 |  |  |  |  | 39.6072
0.625 | 0.545 | 0.00162 | [17 empty] | 65.88 | 75.57 |  | 75.569 |  | 82.8236 | 2.125 |  | 82.8236 |  |  |  |  | 82.8236
0.75 | 0.666 | 0.0024192 | [17 empty] | 115.9 | 131.2 |  | 131.202 |  | 143.7974 | 2.625 |  | 143.7974 |  |  |  |  | 143.7974
0.875 | 0.785 | 0.003361 | [17 empty] | 184.62 | 208.98 |  | 208.98 |  | 229.0421 | 3.125 |  | 229.0421 |  |  |  |  | 229.0421
1.125 | 1.025 | 0.0057303 | [17 empty] | 273.54 | 309.64 |  | 309.638 |  | 339.3632 | 3.625 |  | 339.3632 |  |  |  |  | 339.3632
1.375 | 1.265 | 0.0087279 | [17 empty] | 385.08 | 435.9 |  | 435.902 |  | 477.7486 | 4.125 |  | 477.7486 |  |  |  |  | 477.7486
1.625 | 1.505 | 0.012354 | [17 empty] | 686.18 | 776.72 |  | 776.722 |  | 851.2873 | 5.125 |  | 851.2873 |  |  |  |  | 851.2873
2.125 | 1.985 | 0.021491 | [17 empty] | 1099.1 | 1244.13 |  | 1244.116 |  | 1363.5511 | 6.125 |  | 1363.5511 |  |  |  |  | 1363.5511
2.625 | 2.465 | 0.033141 | [17 empty] | 2268.62 | 2567.98 |  | 2567.98 |  | 2814.5061 | 8.125
3.125 | 2.945 | 0.047304
3.625 | 3.425 | 0.063981
4.125 | 3.905 | 0.083171
5.125 | 4.875 | 0.12962
6.125 | 5.845 | 0.18634
8.125 | 7.725 | 0.32548

## R-410A_Equivalent_Length
Fitting Losses in Equivalent Feet of Pipe (Table 16 2006 ASHRAE REFRIGERATION & Table 4 McQuay AG31-011)
| Smooth Bend Elbows | [5 empty] | Smooth Bend Tee |  |  |  | Valve Losses in Equivalent Feet of Pipe (Table 18 2006 ASHRAE REFRIGERATION, Table 5 McQuay AG31-011)
Click here to select fitting. | 90° Std Elbow | 90° Long Radius Elbow | 90° Street Elbow | 45° Std Elbow | 45° Street Elbow | 180° Std Elbow | Flow Through Branch | Straight-Through Flow No Reduction | Straight-Through Flow Reduced 1/4 | Straight-Through Flow Reduced 1/2 | Globe or Solenoid Valve | 60° Wye Valve | 45° Wye Valve | Angle Valve | Gate Valve | Swing Check | Sight Glass | Filter Drier | Suction Filter | Other
0.5 | 1.4 | 0.9 | 2.3 | 0.7 | 1.1 | 2.3 | 2.7 | 0.9 | 1.2 | 1.4 | 17 | 8 | 6 | 6 | 0.6 | 5 | 1 | 12 | 15 | -1
0.75 | 1.5 | 0.95 | 2.4 | 0.75 | 1.2 | 2.4 | 2.85 | 0.95 | 1.3 | 1.5 | 17.5 | 8.5 | 6.5 | 6.5 | 0.65 | 5.5 | 1.1 | 13.5 | 16 | -1
0.625 | 1.6 | 1 | 2.5 | 0.8 | 1.3 | 2.5 | 3 | 1 | 1.4 | 1.6 | 18 | 9 | 7 | 7 | 0.7 | 6 | 1.2 | 15 | 17 | -1
0.875 | 2 | 1.4 | 3.2 | 0.9 | 1.6 | 3.2 | 4 | 1.4 | 1.9 | 2 | 22 | 11 | 9 | 9 | 0.9 | 8 | 1.6 | 21 | 22 | -1
1.125 | 2.6 | 1.7 | 4.1 | 1.3 | 2.1 | 4.1 | 5 | 1.7 | 2.2 | 2.6 | 29 | 15 | 12 | 12 | 1 | 10 | 2 | 26 | 25 | -1
1.375 | 3.3 | 2.3 | 5.6 | 1.7 | 3 | 5.6 | 7 | 2.3 | 3.1 | 3.3 | 38 | 20 | 15 | 15 | 1.5 | 14 | 2.5 | 35 | 36 | -1
1.625 | 4 | 2.6 | 6.3 | 2.1 | 3.4 | 6.3 | 8 | 2.6 | 3.7 | 4 | 43 | 24 | 18 | 18 | 1.8 | 16 | 2.6 | -1 | 40 | -1
2.125 | 5 | 3.3 | 8.2 | 2.6 | 4.5 | 8.2 | 10 | 3.3 | 4.7 | 5 | 55 | 30 | 24 | 24 | 2.3 | 20 | -1 | -1 | -1 | -1
2.625 | 6 | 4.1 | 10 | 3.2 | 5.2 | 10 | 12 | 4.1 | 5.6 | 6 | 69 | 35 | 29 | 29 | 2.8 | 25 | -1 | -1 | -1 | -1
3.125 | 7.5 | 5 | 12 | 4 | 6.4 | 12 | 15 | 5 | 7 | 7.5 | 84 | 43 | 35 | 35 | 3.2 | 30 | -1 | -1 | -1 | -1
3.625 | 9 | 5.9 | 15 | 4.7 | 7.3 | 15 | 18 | 5.9 | 8 | 9 | 100 | 50 | 41 | 41 | 4 | 35 | -1 | -1 | -1 | -1
4.125 | 10 | 6.7 | 17 | 5.2 | 8.5 | 17 | 21 | 6.7 | 9 | 10 | 120 | 58 | 47 | 47 | 4.5 | 40 | -1 | -1 | -1 | -1
5.125 | 13 | 8.2 | 21 | 6.5 | 11 | 21 | 25 | 8.2 | 12 | 13 | 140 | 71 | 58 | 58 | 6 | 50 | -1 | -1 | -1 | -1
6.125 | 16 | 10 | 25 | 7.9 | 13 | 25 | 30 | 10 | 14 | 16 | 170 | 88 | 70 | 70 | 7 | 60 | -1 | -1 | -1 | -1
8.125 | 20 | 13 | -1 | 10 | -1 | 33 | 40 | 13 | 18 | 20 | 220 | 115 | 85 | 85 | 9 | 80 | -1 | -1 | -1 | -1
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Notes:
Value of -1 in the table represents No data, and prompts the user to enter a value.
In order to search the entire table, the IF() statement needed to be written 4 times (1st - 4th Attempt) due to the limits of the IF() statement in Excel for the Liquid & Suction line componenets below.
Liquid Line Components | [10 empty] | Suction Line Components | [5 empty] | Discharge Line Components |  |  |  |  | HGBP Line Components
Liquid Line Size | 0.75 | [9 empty] | Suction Line Size | 1.375 |  |  |  |  | Discharge Line Size | 1.375 |  |  |  | HGBP Line Size | 0.625
1st Component |  |  |  |  | 4th Component | [5 empty] | 1st Component | [5 empty] | 1st Component |  |  |  |  | 1st Component
90° Std Elbow | 1.5 | 1st Attempt | 1.5 | FT | Sight Glass | FALSE | 1st Attempt | 1.1 | FT |  | 90° Std Elbow | 3.3 | 1st Attempt | 3.3 | FT |  | 90° Std Elbow | 3.3 | 1st Attempt | 3.3 | FT | 90° Std Elbow | 1.4 | 1st Attempt | 1.4 | FT
| FALSE | 2nd Attempt | 8 | QTY |  | FALSE | 2nd Attempt | 1 | QTY |  |  | FALSE | 2nd Attempt | 8 | QTY |  |  | FALSE | 2nd Attempt | 8 | QTY |  | FALSE | 2nd Attempt | 8 | QTY
| FALSE | 3rd Attempt | 12 | FT |  | FALSE | 3rd Attempt | 1.1 | FT |  |  | FALSE | 3rd Attempt | 26.4 | FT |  |  | FALSE | 3rd Attempt | 26.4 | FT |  | FALSE | 3rd Attempt | 11.2 | FT
| FALSE | 4th Attempt |  |  |  | 1.1 | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  | FALSE | 4th Attempt
2nd Component |  |  |  |  | 5th Component | [5 empty] | 2nd Component | [5 empty] | 2nd Component |  |  |  |  | 2nd Component
45° Std Elbow | FALSE | 1st Attempt | 0.75 | FT | Filter Drier | FALSE | 1st Attempt | 13.5 | FT |  | 45° Std Elbow | FALSE | 1st Attempt | 1.7 | FT |  | 45° Std Elbow | FALSE | 1st Attempt | 1.7 | FT | 45° Std Elbow | FALSE | 1st Attempt | 0.7 | FT
| 0.75 | 2nd Attempt | 0 | QTY |  | FALSE | 2nd Attempt | 1 | QTY |  |  | 1.7 | 2nd Attempt | 0 | QTY |  |  | 1.7 | 2nd Attempt | 0 | QTY |  | 0.7 | 2nd Attempt | 0 | QTY
| FALSE | 3rd Attempt | 0 | FT |  | FALSE | 3rd Attempt | 13.5 | FT |  |  | FALSE | 3rd Attempt | 0 | FT |  |  | FALSE | 3rd Attempt | 0 | FT |  | FALSE | 3rd Attempt | 0 | FT
| FALSE | 4th Attempt |  |  |  | 13.5 | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  | FALSE | 4th Attempt
3rd Component |  |  |  |  | 6th Component | [5 empty] | 3rd Component | [5 empty] | 3rd Component |  |  |  |  | 3rd Component
Globe or Solenoid Valve | FALSE | 1st Attempt | 17.5 | FT | Click here to select fitting. | 0 | 1st Attempt | 0 | FT |  | Click here to select fitting. | 0 | 1st Attempt | 0 | FT |  | Click here to select fitting. | 0 | 1st Attempt | 0 | FT | Globe or Solenoid Valve | FALSE | 1st Attempt | 17 | FT
| FALSE | 2nd Attempt | 1 | QTY |  | FALSE | 2nd Attempt | 0 | QTY |  |  | FALSE | 2nd Attempt | 0 | QTY |  |  | FALSE | 2nd Attempt | 0 | QTY |  | FALSE | 2nd Attempt | 1 | QTY
| 17.5 | 3rd Attempt | 17.5 | FT |  | FALSE | 3rd Attempt | 0 | FT |  |  | FALSE | 3rd Attempt | 0 | FT |  |  | FALSE | 3rd Attempt | 0 | FT |  | 17 | 3rd Attempt | 17 | FT
| FALSE | 4th Attempt |  |  |  | FALSE | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  |  | FALSE | 4th Attempt |  |  |  | FALSE | 4th Attempt

## R-410A_Min_Suction_Riser_Cap
2006 ASHRAE Handbook Refrigeration |  |  |  |  | Table Data |  | Inputs |  | Calculated Data
Table 12 (App Guide) Minimum Refrigeration Capacity in Tons for Oil Entrainment up Suction Risers
Saturated Suction Temperature | Suction Superheat | Pipe O.D. (Inches)
|  | 0.5 | 0.625 | 0.75 | 0.875 | 1.125 | 1.375 | 1.625 | 2.125 | 2.625 | 3.125 | 3.625 | 4.125
Area (in2)
oF | oF | 0.146 | 0.233 | 0.348 | 0.484 | 0.825 | 1.256 | 1.78 | 3.094 | 4.77 | 6.812 | 9.213 | 11.97
0 | 10 | 0.167 | 0.317 | 0.542 | 0.833 | 1.67 | 2.92 | 4.58 | 9.58 | 17.17 | 26.67 | 40 | 55.83
20 | 10 | 0.192 | 0.363 | 0.667 | 0.958 | 1.96 | 3.42 | 5.33 | 11.08 | 19.58 | 30.83 | 45.83 | 64.17
40 | 10 | 0.213 | 0.4 | 0.683 | 1.067 | 2.17 | 3.75 | 6 | 12.42 | 21.67 | 35 | 51.67 | 71.67
Suction Superheat | 10
| oF |  |  |  | Min. Suction Riser Capacity - Curve Fit |  |  |  | Info Found Below Table 12 (App Guide) | [7 empty] | Min. Suction Riser Capacity - Curve Fit w/Multiplier
Type L Copper, OD | Saturated Suction Temperature, oF |  |  |  | SST | Type L Copper, OD | Superheat |  |  |  | Interpolation of Suction & Discharge Multipliers | [7 empty] | Determines Minimum Suction Riser Size |  |  |  | Determines Suction Riser Capacity
[5 empty] | oF |  | 10 |  | Condensing Temperature | R-410A | Act. Cond. Temp. | Min # for Interpolation | Max # for Interpolation | Known x's | Known y's Suction | Suction Riser |  |  | Min. Suction Capacity | Look Up Sufficient Suction Line Capacity | Determine Minimum Suction Line Capacity | Corresponding Suction Riser Size, OD | Table 3 - Curve Fit w/ Suction Multiplier
| 0 | 20 | 40 |  | 40 | inches | oF | [9 empty] | Suction Riser Capacity | Type L Copper, OD |  |  |  |  | Type L Copper, OD | Suction Line Capacity | Size of Suction Riser | Riser Capacity
0.5 | 0.167 | 0.192 | 0.213 |  |  | 0.5 | 0.215 |  | oF | multiplier | oF |  |  |  |  | multiplier |  |  | tons
0.625 | 0.317 | 0.363 | 0.4 |  |  | 0.625 | 0.401 |  | 80 | 1.05 | 120 | 80 |  | 120 | 0.83 | 0.83 | tons | inches | 8.9 |  |  |  |  | tons | inches | tons
0.75 | 0.542 | 0.667 | 0.683 |  |  | 0.75 | 0.742 |  | 90 | 1 |  | 90 |  | 120 | 0.83 |  | 0.17845 | 0.5 |  | 0.17845 | 4.98 | 1.625 | 0.5 | 0.78792 | 1.375 | 13.7368
0.875 | 0.833 | 0.958 | 1.067 |  |  | 0.875 | 1.069 |  | 100 | 0.94 |  | 100 |  |  |  |  | 0.33283 | 0.625 |  | 0.33283 |  |  | 0.625 | 1.4455
1.125 | 1.67 | 1.96 | 2.17 |  |  | 1.125 | 2.17 |  | 110 | 0.9 |  | 110 |  |  |  |  | 0.61586 | 0.75 |  | 0.61586 |  | 1.375 | 0.75 | 2.506
1.375 | 2.92 | 3.42 | 3.75 |  |  | 1.375 | 3.768 |  | 120 | 0.83 |  | 120 | 120 |  |  |  | 0.88727 | 0.875 |  | 0.88727 |  | checks to make sure scution riser isn't | 0.875 | 3.8491
1.625 | 4.58 | 5.33 | 6 |  |  | 1.625 | 6 |  | 130 | 0.77 |  |  | 130 |  |  |  | 1.8011 | 1.125 |  | 1.8011 |  | larger than horizontal suction pipe | 1.125 | 7.9165
2.125 | 9.58 | 11.08 | 12.42 |  |  | 2.125 | 12.42 |  | 140 | 0.72 |  |  | 140 |  |  |  | 3.1274 | 1.375 |  | 3.1274 |  | 3.1274 | 1.375 | 13.7368
2.625 | 17.17 | 19.58 | 21.67 |  |  | 2.625 | 21.67 | [9 empty] | 4.98 | 1.625 |  | 4.98 |  | capacity for above line size | 1.625 | 21.5725
3.125 | 26.67 | 30.83 | 35 |  |  | 3.125 | 34.998 | [9 empty] | 10.3086 | 2.125 |  |  |  |  | 2.125 | 44.5816
3.625 | 40 | 45.83 | 51.67 |  |  | 3.625 | 51.664 | [9 empty] | 17.9861 | 2.625 |  |  |  |  | 2.625 | 78.4249
4.125 | 55.83 | 64.17 | 71.67 |  |  | 4.125 | 71.59 | [9 empty] | 29.0483 | 3.125 |  |  |  |  | 3.125 | 124.9205
[17 empty] | 42.8811 | 3.625 |  |  |  |  | 3.625 | 185.1538
[17 empty] | 59.4197 | 4.125 |  |  |  |  | 4.125 | 260.7526
[23 empty] | 5.125 | 464.3087
[23 empty] | 6.125 | 745.238

## R-410A_Min_Hot-Gas_Riser_Cap
2006 ASHRAE Handbook Refrigeration |  |  |  |  | Table Data |  | Inputs |  | Calculated Data
Table 16 (App Guide) Minimum Refrigeration Capacity in Tons for Oil Entrainment up Hot-Gas Risers
Saturated Temperature | Discharge Superheat | Pipe O.D. (Inches)
|  | 0.5 | 0.625 | 0.75 | 0.875 | 1.125 | 1.375 | 1.625 | 2.125 | 2.625 | 3.125 | 3.625 | 4.125
Area (in2)
oF | oF | 0.146 | 0.233 | 0.348 | 0.484 | 0.825 | 1.256 | 1.78 | 3.094 | 4.77 | 6.812 | 9.213 | 11.97
80 | 60 | 0.33 | 0.61 | 1.06 | 1.59 | 3.19 | 5.54 | 8.75 | 13.8 | 24.4 | 38.9 | 57.8 | 81.7
100 | 60 | 0.34 | 0.628 | 1.092 | 1.638 | 3.29 | 5.71 | 9.01 | 14.21 | 25.13 | 40.04 | 59.53 | 84.15
120 | 60 | 0.35 | 0.647 | 1.125 | 1.687 | 3.38 | 5.88 | 9.28 | 14.64 | 25.89 | 41.27 | 61.32 | 86.68
Discharge Superheat | 60 |  |  |  |  | Min. Discharge Riser Capacity - Curve Fit | [10 empty] | Min. Discharge Riser Capacity - Curve Fit w/Multiplier
| oF |  |  |  | Condensing Temperature |  |  |  | Info Found Below Table 16 (App Guide) | [9 empty] | Determines Minimum Discharge Riser Size |  |  |  | Determines Discharge Riser Capacity
Type L Copper, OD | [5 empty] | Type L Copper, OD | Superheat |  |  |  | Interpolation of Discharge Multipliers | [7 empty] | Min. Discharge Capacity | Look Up Sufficient Discharge Line Capacity | Determine Minimum Discharge Line Capacity | Corresponding Discharge Riser Size, OD | Table 3 - Curve Fit w/ Discharge Multiplier
| Saturated Discharge Temperature, oF |  |  |  | oF |  | 30 |  | Saturated Suction Temp | R-410A | Act. SST | Min # for Interpolation | Max # for Interpolation | Known x's | Known y's Discharge | Discharge Riser | Discharge Riser Capacity | Type L Copper, OD |  |  |  |  | Type L Copper, OD | Discharge Line Capacity | Size of Discharge Riser | Riser Capacity
| 80 | 100 | 120 |  | 120 | inches | oF | [11 empty] | tons
0.5 | 0.33 | 0.34 | 0.35 |  | cond + superheat = discharge temp | 0.5 | 0.35 |  | oF | multiplier | oF |  |  |  |  | multiplier | tons | inches | N/A |  |  |  |  | tons | inches | tons
0.625 | 0.61 | 0.628 | 0.647 |  |  | 0.625 | 0.6464 |  | 0 | 0.9 | 40 | 0 |  | 40 | 1 | 1 | 0.35 | 0.5 |  | 0.35 | 86.68 | 4.125 | 0.5 | 1.4577 | 1.375 | 25.0776
0.75 | 1.06 | 1.092 | 1.125 |  |  | 0.75 | 1.1244 |  | 20 | 0.94 |  | 20 |  | 40 | 1 |  | 0.6464 | 0.625 |  | 0.6464 |  |  | 0.625 | 2.7279
0.875 | 1.59 | 1.638 | 1.687 |  |  | 0.875 | 1.6864 |  | 40 | 1 |  | 40 | 40 |  |  |  | 1.1244 | 0.75 |  | 1.1244 |  | 1.375 | 0.75 | 4.635
1.125 | 3.19 | 3.29 | 3.38 |  |  | 1.125 | 3.41 |  | 60 | 1.06 |  |  | 60 |  |  |  | 1.6864 | 0.875 |  | 1.6864 |  | checks to make sure discharge riser isn't | 0.875 | 7.1459
1.375 | 5.54 | 5.71 | 5.88 |  |  | 1.375 | 5.88 | [9 empty] | 3.41 | 1.125 |  | 3.41 |  | larger than horizontal discharge pipe | 1.125 | 14.4332
1.625 | 8.75 | 9.01 | 9.28 |  |  | 1.625 | 9.238 | [9 empty] | 5.88 | 1.375 |  | 5.88 |  | 5.88 | 1.375 | 25.0776
2.125 | 13.8 | 14.21 | 14.64 |  |  | 2.125 | 14.568 | [9 empty] | 9.238 | 1.625 |  | 9.238 |  | capacity for above line size | 1.625 | 39.6072
2.625 | 24.4 | 25.13 | 25.89 |  |  | 2.625 | 25.92 | [9 empty] | 14.568 | 2.125 |  | 14.568 |  |  | 2.125 | 82.8236
3.125 | 38.9 | 40.04 | 41.27 |  |  | 3.125 | 41.096 | [9 empty] | 25.92 | 2.625 |  | 25.92 |  |  | 2.625 | 143.7974
3.625 | 57.8 | 59.53 | 61.32 |  |  | 3.625 | 61.392 | [9 empty] | 41.096 | 3.125 |  | 41.096 |  |  | 3.125 | 229.0421
4.125 | 81.7 | 84.15 | 86.68 |  |  | 4.125 | 86.68 | [9 empty] | 61.392 | 3.625 |  | 61.392 |  |  | 3.625 | 339.3632
[17 empty] | 86.68 | 4.125 |  | 86.68 |  |  | 4.125 | 477.7486
[23 empty] | 5.125 | 851.2873
[23 empty] | 6.125 | 1363.5511